## Slide 1: 2011 Combate a Enchentes Sistema de Reservatórios no Braço Principal do Rio Missouri
Jerry W. Webb, P.E., D.WRE
Principal Hydrologic & Hydraulic Engineer
Hydrology, Hydraulics & Coastal Community of Practice Leader
US Army Corps of Engineers, Headquarters
Jerry.w.webb@usace.army.mil
Dam Safety Workshop
Brasília, Brazil
20-24 May 2013

## Slide 2: Operação Mighty Missouri
Vídeo da Enchente de 2011

## Slide 3
North Dakota
Sistema de Reservatórios do Braço Principal do Rio Missouri
3745 km de extensão
17% de EUA continental
Notes: Missouri River 2341 mi long, 1/6 of continental U.S.
Upper 1/3 – Source of 2011 flood.
Middle 1/3 – 6 mainstem reservoirs Ft Peck to Gavins Point.
Lower 1/3 – levees along both sides of river (focus of this presentation)
Floodplain >5 mi wide, heavy agricultural use with some urban areas including Sioux City, Omaha, Council Bluffs, Kansas City, St. Louis.

## Slide 4
Notes: Note reservoir size of Ft Peck, Garrison, and Oahe.

## Slide 5: Enchente de 2011 Significado Operacional
Cota Alta Recorde vivida em Fort Peck, Garrison, Oahe, e Fort Randall.
  Níveis d’água em Fort Peck e Garrison entraram em zonas de sobrecarga.
Decarga Máxima do Projeto (65kcfs – 160kcfs) Excedeu os Registros Operacionais Históricos em Aproximadamente 250%.
  Primeira vez que extravasores de Garrison Big Bend foram utilizados.
  Primeira vez que túneis de enchentes de Fort Randall foi usado.
Liberação Contínua para Controle de Cheias de Maio a Dezembro. Liberação de pico mantida por quase dois meses em cada projeto.

## Slide 6: Vigilância de Enchentes para Segurança de Barragens em 2011
Planejamento da Vigilância
  Pessoal técnico de OD & ED em Cada Equipe
  Equipes Múltiplas em Turnos Contínuos (turnos de 2 semanas)
  Líder da Equipe de Vigilãncia (Engenheiro de Segurança de Barragens)
  Escritório de Campo Temporário (Equipamentos, Arquivos, Apoios diversos)
  Vigilância Remota por Vídeo e Plantas Leves
  Restrições de Acesso ao Público, Segurança e Controle de Multidões
Atividades de Vigilância
  Inspeções
  Leituras de Instrumentação & Análise de Dados
  Comunicação – Relatórios Diários, Briefings (OPM, EOC)
  Medidas Temporárias de Mitigação

## Slide 7: Barragem Fort Peck
Maciço Principal
Bacia de Amortecimento
Extravasor

## Slide 8
Vertedouro de Fort Peck
Erosão na bacia de amortecimento em 2011
Notes: Enormous Hydrauilic Fill Dam. First Dam to ever use Relief wells to control underseepage.
75 yr old Spillway in Bearpaw Shale, very erosive and unstable
No Stilling basin, only vertical cutoff wall that extended 70 feet down
Considerable historical movement experienced down chute and damage to underdrain system;
Several documented concerns regarding stability of cutoff structure and chute slabs
Spillway flows were double previously experienced

## Slide 9
Vertedouro Fort Peck

## Slide 10: Barragem Garrison
Cota operacional máxima | 565,09 m
Base exclusivamente para Controle de Enchentes | 563,88 m
Base para Controle de Enchentes | 5600,7 feet
 | 1955-2010 | 2011
Cota Máxima Histórica (Data) | 565.48 m (1975) | 1854.6 feet (July 1, 2011)
Maximum Daily Average Release (Date) | 1840 m3/s (1975) | 4264.5 cfs (25 junho, 2011)
Casa de Força
Vertedouro

## Slide 11
Erosão no Vertedouro e subpressão potencial
Infiltração na ombreira esquerda
Atividade inicial de D Dolina
Solapamento de canal de fuga
West abutment seepage
Barragem Garrison
Notes: Garrison Dam – Historic Movement along upstream face and underseepage in right terrace due to flaw in underseepage cutoff.
Main Concern was 1st time use of Spillway

## Slide 12
“Rabo de galo” causado
por destaque de placas
Destaque de placas em laje do vertedouro
Barragem Garrison

## Slide 13
Empreiteira repara desplacamento de laje de concreto no vertedouro da Barragem Garrison

## Slide 14: Barragem Oahe
 | 1962-2010 | 2011
Elevação Histórica Máxima da Cota | 493.5 m (1995 & 1996) | 493,81 m (June 26, 2011)
Maximum Daily Average Release (Date) | 1670 m3/s (1997) | 4539.19 m3/s (20 junho, 2011)
Cota operacional mácima | 493,9 m
Base exclusiva para control de enchentes | 492,98 m
Base para Controle de Enchentes | 490,09 feet
Casa de Força
Bacia de Dissipação na Descarga

## Slide 15
Notes: Flood Tunnel Releases, rarely used, releases were in excess of 200% of previous max
History of severe cavitation that was repaired in the 90s, but never tested
After confidence was gained in Spillway, release flexibilities enabled ROV inspection.

## Slide 16
Erosão observada em muros da ala direita e esquerda
Reparos de Emergência Concluídos
Alta vazão de descarga à bacia de dissipação

## Slide 17: Barragem Big Bend
 | 1964-2010 | 2011
Maximum Pool Elevation (Date) | 1422.1 feet (1991) | 1421.5 feet (June 22, 2011)
Maximum Daily Average Release (Date) | 74,000 cfs (1997) | 165,000 cfs (June 23, 2011)
Max Operating Pool | 1423.0 feet
Base of Exclusive Flood Control | 1422.0 feet
Base of Flood Control | 1420.0 feet
Primary Dam Safety Issues: 1. Spillway Erosion
2. Left Abutment Seepage
Casa de Força
Vertedouro

## Slide 18
Erosão atrás de muro de ala devido à alta vazão de descarga do vertedouro

## Slide 19: Barragem Big Bend, SD – Danos pelo galgamento no vertedouro
Photo here

## Slide 21
July 1 – Cota em Fort Randall de aprox. 418.59 m
Erosão e Solapamento
de reaterro granular
Observe estrutura cedendo.
Lajes subaquáticos falharam, erodindo
parte superior de 1,5 a 2.43 m abaixo do topo
dos muros da bacia
New Piezometers
Notes: Surveillance personnel observed what was thought to be panels of slabs being uplifted
Spillway temporarily shut downs to permit inspection with SONAR device to verify condition, assure materials were not ball milling, assess erosion and install monitoring devices.
Granular backfill behind walls tied into a embankmnent toe train and was being eroded
Tailwater still projected to climb, decision was made to place riprap to slow down erosion and lessen potential for undermining toe of embankment.

## Slide 22
Notes: Slabs blew out and backfill washed away

## Slide 23: Levantamentos com LIDAR e SONAR

## Slide 24
Notes: Project Forces performed work with emergency stockpile materials

## Slide 26
Notes: Discharges through Spillway more common, but no where near this magnitude or duration.
Some of the gates were under minor repair and could not be in operation during initial stages
Unbalanced loading and long duration of discharges had unexpectedly charged and pressurized the granular wall backfill to the higher elevations.

## Slide 27
Barragem Fort Randall – Deterioração de Laje de Vertedouro
Notes: Temporarily shut down spillway to perfrom patching repairs and closed off (grouted) drain openings

## Slide 28
Chart: Flow in 1000 cfs
Flood Stage
Missouri River at Sioux City, IA
Actual and Unregulated Flows
Estágio de Enchente = 9.14 m
(~ 3454 m3/s)
Notes: Run off from the snow melt and rain filled flood storage of all six maintem reserviors.
Red line shows unregulated – flows without dams in place.
Gray area shows the 2011 flood flows, a few miles downstream of Gavins Pt dam.
Long duration: June – September
Reservoir system effective at removing peak of hydrograph.
Some public perception in lower basin: “Man made flood.”

## Slide 29: Resumo de Combate a Enchentes
Valor de bons planos de Vigilância
Antecipar erosão devido a grandes descargas durante enchentes
É preciso ter recursos disponíveis na hora de ações emergenciais (intervenção).

## Slide 30
OBRIGADO